## Sheet1
MODBUS Protocol for IoT Series
1. Introduction
MODBUS TCP protocol
2. Physical Layer
Communication port : Ethernet TCP/IP
Asynchronous format : 한 character는 10로 구성된다.(1 start bit + 8 data bits + (No parity bit) + 1 stop bit)
Parity : no parity
Master-Slave 방식으로 Master만이 요청(request)을 할 수 있고, Slave들은 Master에게 요청된 데이터를 보내주거나
질의에서 요청되는 동작을 수행하는 응답(response)을 한다.
3. Data Link Layer
Master가 Slave에게 요청 프레임을 보내면, Slave는 응답프레임을 보낸다.
각 프레임들은 dead time에 의해 구별된다.
다음은 프레임을 보내고 받는 일반적인 형식이다.
| DESCRIPTION |  | SIZE
| SLAVE ADDRESS |  | 1 byte
| FUNCTION CODE |  | 1 byte
| DATA |  | N byte
| CRC |  | 2 byte
| DEAD TIME |  | 3.5 bytes transmission time
1) SLAVE ADDRESS
- Server address range : 1~247 decimal
- Master가 Slave에게 요청을 하는 프레임의 Slave device address 영역이 0인 경우는
Master device가 모든 Slave에게 broadcasting함을 의미한다. (Time Sync 요청에만 동작함)
- Master가 Slave에게 요청을 하는 경우에 address field에는 해당 Slave address를 기입하여 전송한다.
- Slave가 Master에게 응답을 하는 경우에 address field에는 자신의 주소를 기입하여 전송한다.
2) FUNCTION CODE
- Valid range : 1~255
- Normal : 1~127, Error : 129 ~ 255(normal + 0x80)
- Master가 Slave에게 요구하는 내용을 정의한 것이다.
- Slave는 다음과 같은 정보를 기입한다.
Normal response의 경우 : request의 function code값을 그대로 echo
Exception response의 경우 : request의 function code값의 MSB를 1로 set하여 기입한다.
3) DATA
- Register address
- 요청 또는 처리할 item의 양
- 실제 데이터의 바이트 수
4) CRC
- 16bit MODBUS crc
4. MODBUS Exception codes
| code | Name
| 01h | ILLEGAL FUNCTION
| 02h | ILLEGAL DATA ADDRESS
| 03h | ILLEGAL DATA VALUE
| 04h | SLAVE DEVICE FAILURE
| 05h | ACKNOWLEDGE
| 06h | SLAVE DEVICE BUSY
| 10h | Event/Fault record 데이터 없음
| 11h | SBO TIME OUT
| 12h | ILLEGAL ADU LENGTH
| 13h | LOCAL MODE
| 14h | MAIN_NAK
<중요사항>
Max register read count : 56
(03h, 04h) : 한 레지스터를 읽을 수도 있고, 여러 개를 읽을 수도 있는데
여러 개를 읽을 경우 최대 56레지스터까지 읽을 수 있다.
5. Function Code Description
| code | Description
| 03h | Read Holding Registers
| 04h | Read Input Registers
| 05h | Write Single Coil
| 16h | Write Multiple Registers
6. IoT Address Map (IoT -> PLC)
Register | Register Name |  |  | Range | Unit | Data Type | 속성
30001 | Main Power R Phase Voltage PV |  |  | 0 ~ 65535 | V | UINT | R | Main Power R Phase Voltage PV
30002 | Main Power S Phase Voltage PV |  |  | 0 ~ 65535 | V | UINT | R | Main Power S Phase Voltage PV
30003 | Main Power T Phase Voltage PV |  |  | 0 ~ 65535 | V | UINT | R | Main Power T Phase Voltage PV
30004 | Pump #1 R Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #1 R Phase Current PV
30005 | Pump #1 S Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #1 S Phase Current PV
30006 | Pump #1 T Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #1 T Phase Current PV
30007 | Pump #1 Vibration PV |  |  | 0 ~ 65535 | cm/sec² | UINT | R | Pump #1 Vibration PV
30008 | Pump #1 Bearing Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #1 Bearing Temperature
30009 | Pump #1 Motor Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #1 Motor Temperature
30010 | Pump #1 Prediction Data |  |  | 0 ~ 65535 |  | UINT | R | Pump #1 Prediction Data
30011 | Pump #2 R Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #2 R Phase Current PV
30012 | Pump #2 S Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #2 S Phase Current PV
30013 | Pump #2 T Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #2 T Phase Current PV
30014 | Pump #2 Vibration PV |  |  | 0 ~ 65535 | cm/sec² | UINT | R | Pump #2 Vibration PV
30015 | Pump #2 Bearing Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #2 Bearing Temperature
30016 | Pump #2 Motor Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #2 Motor Temperature
30017 | Pump #2 Prediction Data |  |  | 0 ~ 65535 |  | UINT | R | Pump #2 Prediction Data
30018 | Pump #3 R Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #3 R Phase Current PV
30019 | Pump #3 S Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #3 S Phase Current PV
30020 | Pump #3 T Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #3 T Phase Current PV
30021 | Pump #3 Vibration PV |  |  | 0 ~ 65535 | cm/sec² | UINT | R | Pump #3 Vibration PV
30022 | Pump #3 Bearing Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #3 Bearing Temperature
30023 | Pump #3 Motor Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #3 Motor Temperature
30024 | Pump #3 Prediction Data |  |  | 0 ~ 65535 |  | UINT | R | Pump #3 Prediction Data
30025 | Pump #4 R Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #4 R Phase Current PV
30026 | Pump #4 S Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #4 S Phase Current PV
30027 | Pump #4 T Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #4 T Phase Current PV
30028 | Pump #4 Vibration PV |  |  | 0 ~ 65535 | cm/sec² | UINT | R | Pump #4 Vibration PV
30029 | Pump #4 Bearing Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #4 Bearing Temperature
30030 | Pump #4 Motor Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #4 Motor Temperature
30031 | Pump #4 Prediction Data |  |  | 0 ~ 65535 |  | UINT | R | Pump #4 Prediction Data
30032 | Pump #5 R Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #5 R Phase Current PV
30033 | Pump #5 S Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #5 S Phase Current PV
30034 | Pump #5 T Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #5 T Phase Current PV
30035 | Pump #5 Vibration PV |  |  | 0 ~ 65535 | cm/sec² | UINT | R | Pump #5 Vibration PV
30036 | Pump #5 Bearing Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #5 Bearing Temperature
30037 | Pump #5 Motor Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #5 Motor Temperature
30038 | Pump #5 Prediction Data |  |  | 0 ~ 65535 |  | UINT | R | Pump #5 Prediction Data
30039 | Pump #6 R Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #6 R Phase Current PV
30040 | Pump #6 S Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #6 S Phase Current PV
30041 | Pump #6 T Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #6 T Phase Current PV
30042 | Pump #6 Vibration PV |  |  | 0 ~ 65535 | cm/sec² | UINT | R | Pump #6 Vibration PV
30043 | Pump #6 Bearing Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #6 Bearing Temperature
30044 | Pump #6 Motor Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #6 Motor Temperature
30045 | Pump #6 Prediction Data |  |  | 0 ~ 65535 |  | UINT | R | Pump #6 Prediction Data
30046 | Pump #7 R Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #7 R Phase Current PV
30047 | Pump #7 S Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #7 S Phase Current PV
30048 | Pump #7 T Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #7 T Phase Current PV
30049 | Pump #7 Vibration PV |  |  | 0 ~ 65535 | cm/sec² | UINT | R | Pump #7 Vibration PV
30050 | Pump #7 Bearing Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #7 Bearing Temperature
30051 | Pump #7 Motor Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #7 Motor Temperature
30052 | Pump #7 Prediction Data |  |  | 0 ~ 65535 |  | UINT | R | Pump #7 Prediction Data
30053 | Pump #8 R Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #8 R Phase Current PV
30054 | Pump #8 S Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #8 S Phase Current PV
30055 | Pump #8 T Phase Current PV |  |  | 0 ~ 65535 | A | UINT | R | Pump #8 T Phase Current PV
30056 | Pump #8 Vibration PV |  |  | 0 ~ 65535 | cm/sec² | UINT | R | Pump #8 Vibration PV
30057 | Pump #8 Bearing Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #8 Bearing Temperature
30058 | Pump #8 Motor Temperature |  |  | 0 ~ 65535 | ℃ | UINT | R | Pump #8 Motor Temperature
30059 | Pump #8 Prediction Data |  |  | 0 ~ 65535 |  | UINT | R | Pump #8 Prediction Data
30060
30061
30062
30063
30064
30065
30066
30067
30068
30069
30070
30071
30072
30073
30074
30075
30076
30077
30078
30079
30080
30081
30082
30083
30084
30085
30086
30087
30088
30089
30090
30091
30092
30093
30094
30095
30096
30097
30098
30099
30100
30101
30102
30103
30104
30105
30106
30107
30108
30109
30110
30111
30112
30113
30114
30115
30116
30117
30118
30119
7. IoT Address Map (PLC -> Iot)
Register | Register Name |  |  | Range | Unit | Data Type | 속성
40001 | Main Power R Phase Voltage PV |  |  | 0 ~ 16000 | V | UINT | W | Main Power R Phase Voltage PV
40002 | Main Power S Phase Voltage PV |  |  | 0 ~ 16000 | V | UINT | W | Main Power S Phase Voltage PV
40003 | Main Power T Phase Voltage PV |  |  | 0 ~ 16000 | V | UINT | W | Main Power T Phase Voltage PV
40004 | Pump #1 R Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #1 R Phase Current PV
40005 | Pump #1 S Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #1 S Phase Current PV
40006 | Pump #1 T Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #1 T Phase Current PV
40007 | Pump #1 Vibration PV |  |  | 0 ~ 16000 | cm/sec² | UINT | W | Pump #1 Vibration PV
40008 | Pump #1 Bearing Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #1 Bearing Temperature
40009 | Pump #1 Motor Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #1 Motor Temperature
40010 | Pump #1 Prediction Data |  |  | 0 ~ 16000 |  | UINT | W | Pump #1 Prediction Data
40011 | Pump #2 R Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #2 R Phase Current PV
40012 | Pump #2 S Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #2 S Phase Current PV
40013 | Pump #2 T Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #2 T Phase Current PV
40014 | Pump #2 Vibration PV |  |  | 0 ~ 16000 | cm/sec² | UINT | W | Pump #2 Vibration PV
40015 | Pump #2 Bearing Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #2 Bearing Temperature
40016 | Pump #2 Motor Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #2 Motor Temperature
40017 | Pump #2 Prediction Data |  |  | 0 ~ 16000 |  | UINT | W | Pump #2 Prediction Data
40018 | Pump #3 R Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #3 R Phase Current PV
40019 | Pump #3 S Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #3 S Phase Current PV
40020 | Pump #3 T Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #3 T Phase Current PV
40021 | Pump #3 Vibration PV |  |  | 0 ~ 16000 | cm/sec² | UINT | W | Pump #3 Vibration PV
40022 | Pump #3 Bearing Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #3 Bearing Temperature
40023 | Pump #3 Motor Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #3 Motor Temperature
40024 | Pump #3 Prediction Data |  |  | 0 ~ 16000 |  | UINT | W | Pump #3 Prediction Data
40025 | Pump #4 R Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #4 R Phase Current PV
40026 | Pump #4 S Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #4 S Phase Current PV
40027 | Pump #4 T Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #4 T Phase Current PV
40028 | Pump #4 Vibration PV |  |  | 0 ~ 16000 | cm/sec² | UINT | W | Pump #4 Vibration PV
40029 | Pump #4 Bearing Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #4 Bearing Temperature
40030 | Pump #4 Motor Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #4 Motor Temperature
40031 | Pump #4 Prediction Data |  |  | 0 ~ 16000 |  | UINT | W | Pump #4 Prediction Data
40032 | Pump #5 R Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #5 R Phase Current PV
40033 | Pump #5 S Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #5 S Phase Current PV
40034 | Pump #5 T Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #5 T Phase Current PV
40035 | Pump #5 Vibration PV |  |  | 0 ~ 16000 | cm/sec² | UINT | W | Pump #5 Vibration PV
40036 | Pump #5 Bearing Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #5 Bearing Temperature
40037 | Pump #5 Motor Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #5 Motor Temperature
40038 | Pump #5 Prediction Data |  |  | 0 ~ 16000 |  | UINT | W | Pump #5 Prediction Data
40039 | Pump #6 R Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #6 R Phase Current PV
40040 | Pump #6 S Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #6 S Phase Current PV
40041 | Pump #6 T Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #6 T Phase Current PV
40042 | Pump #6 Vibration PV |  |  | 0 ~ 16000 | cm/sec² | UINT | W | Pump #6 Vibration PV
40043 | Pump #6 Bearing Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #6 Bearing Temperature
40044 | Pump #6 Motor Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #6 Motor Temperature
40045 | Pump #6 Prediction Data |  |  | 0 ~ 16000 |  | UINT | W | Pump #6 Prediction Data
40046 | Pump #7 R Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #7 R Phase Current PV
40047 | Pump #7 S Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #7 S Phase Current PV
40048 | Pump #7 T Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #7 T Phase Current PV
40049 | Pump #7 Vibration PV |  |  | 0 ~ 16000 | cm/sec² | UINT | W | Pump #7 Vibration PV
40050 | Pump #7 Bearing Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #7 Bearing Temperature
40051 | Pump #7 Motor Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #7 Motor Temperature
40052 | Pump #7 Prediction Data |  |  | 0 ~ 16000 |  | UINT | W | Pump #7 Prediction Data
40053 | Pump #8 R Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #8 R Phase Current PV
40054 | Pump #8 S Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #8 S Phase Current PV
40055 | Pump #8 T Phase Current PV |  |  | 0 ~ 16000 | A | UINT | W | Pump #8 T Phase Current PV
40056 | Pump #8 Vibration PV |  |  | 0 ~ 16000 | cm/sec² | UINT | W | Pump #8 Vibration PV
40057 | Pump #8 Bearing Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #8 Bearing Temperature
40058 | Pump #8 Motor Temperature |  |  | 0 ~ 16000 | ℃ | UINT | W | Pump #8 Motor Temperature
40059 | Pump #8 Prediction Data |  |  | 0 ~ 16000 |  | UINT | W | Pump #8 Prediction Data
40060
40061
40062
40063
40064
40065
40066
40067
40068
40069
40070
40071
40072
40073
40074
40075
40076
40077
40078
40079
40080
40081
40082
40083
40084
40085
40086
40087
40088
40089
40090
40091
40092
40093
40094
40095
40096
40097
40098
40099
40100
40101
40102
40103
40104
40105
40106
40107
40108
40109
40110
40111
40112
40113
40114
40115
40116
40117
40118